## Sheet1 (hidden)
BIHAR STATE POWER TRANSMISSION COMPANY LIMITED
DEPARTMENT OF TRANSMISSION (O & M)
Sl. No. | Name of Transmission Circle | Name of Grid Sub-station | Voltage Lever (220/132KV) | Capacity (in MVA) |  | Voltage Level (132/33 KV) | Capacity (in MVA) |  | Voltage Level (132/25 KV) | Capacity (in MVA)
1 |  | 2 | 3 | 4 |  | 5 | 6 |  | 7 | 8
A | PATNA
1 |  | FATUHA | 220/132KV | 4X100 | 400 | 132/33 KV | 3X50 | 150
2 |  | SIPARA | 220/132 KV | 2X150 | 300 | 132/33 KV | 2X50 | 100
3 |  | KHAGAUL | 220/132 KV | 3X100 | 300 | 132/33 KV | 3X50 | 150
4 |  | BIHTA |  |  |  | 132/33 KV | 2X50 | 100
5 |  | DIGHA |  |  |  | 132/33 KV | 2X50 | 100
6 |  | JAKKANPUR |  |  |  | 132/33 KV | 3X50 +1X20 | 170
7 |  | MITHAPUR |  |  |  | 132/33 KV | 2X50 | 100
8 |  | GAYGHAT |  |  |  | 132/33 KV | 2X50 | 100
9 |  | KATRA |  |  |  | 132/33 KV | 2X50 | 100
10 |  | KARBIGAHIA |  |  |  | 132/33 KV | 4X50 | 200
11 |  | MASAURHI |  |  |  | 132/33 KV | 2X20 | 40
B | BIHARSHARIF
1 |  | BIHARSHARIF (SG) | 220/132 KV | 3X150 | 450 | 132/33 KV | 1X20 | 20
2 |  | BARIPAHARI |  |  |  | 132/33 KV | 2X50 +1X20 | 120
3 |  | HARNAUT |  |  |  | 132/33 KV | 2X20 | 40
4 |  | RAJGIR |  |  |  | 132/33 KV | 2X20 | 40
5 |  | NALANDA |  |  |  | 132/33 KV | 2X20 | 40
6 |  | BARH |  |  |  | 132/33 KV | 2X20 | 40
7 |  | HATHIDAH |  |  |  | 132/33 KV | 3X20 | 60
8 |  | SHIEKHPURA |  |  |  | 132/33 KV | 2X20 | 40
9 |  | EKANGARSARI |  |  |  | 132/33 KV | 2X20 | 40
10 |  | LAKHISARAI |  |  |  | 132/33 KV | 3X20 | 60
11 |  | JAMUI |  |  |  | 132/33 KV | 2X20 | 40
C | GAYA
1 |  | BODHGAYA | 220/132 KV | 3X150 | 450 | 132/33 KV | 2X50 | 100
2 |  | CHANDAUTI |  |  |  | 132/33 KV | 2X50 | 100 | 132/25 KV | 2X13.35 | 26.7
3 |  | BELAGANJ |  |  |  | 132/33 KV | 2X20 | 40
4 |  | JAHANABAD |  |  |  | 132/33 KV | 2X20 | 40
5 |  | ATAULA |  |  |  | 132/33 KV | 2X20 | 40
6 |  | RAFIGANJ |  |  |  | 132/33 KV | 2X20 | 40
7 |  | WAZIRGANJ |  |  |  | 132/33 KV | 2X20 | 40
8 |  | NAWADA |  |  |  | 132/33 KV | 2X20 | 40
9 |  | TEKARI |  |  |  | 132/33 KV | 2X20 | 40
10 |  | SHERGHATI |  |  |  | 132/33 KV | 2X20 | 40
11 |  | HULASHGANJ |  |  |  | 132/33 KV | 2X20 | 40
D | DEHRI-ON-SONE
1 |  | DEHRI-ON-SONE | 220/132 KV | 3X100 +1X50 | 350 | 132/33 KV | 2X50 | 100
2 |  | BANJARI |  |  |  | 132/33 KV | 2X20 | 40
3 |  | MOHANIA |  |  |  | 132/33 KV | 2X20 | 40
4 |  | KARMANASA |  |  |  | 132/33 KV | 1X50 + 2X20 | 90 | 132/25 KV | 1X20 +1X21.6 | 41.6
5 |  | SASARAM |  |  |  | 132/33 KV | 2X20 | 40
6 |  | BIKARMGANJ |  |  |  | 132/33 KV | 2X20 | 40
7 |  | SONENAGAR |  |  |  | 132/33 KV | 1X50 + 1X20 +1X10 | 80 | 132/25 KV | 1X20 + 1 X 21.6 | 41.6
8 |  | AURANGABAD |  |  |  | 132/33 KV | 2X20 | 40
9 |  | GOH |  |  |  | 132/33 KV | 2X20 | 40
10 |  | AARAH |  |  |  | 132/33 KV | 1X50 + 1X20 | 70
11 |  | JAGDISHPUR |  |  |  | 132/33 KV | 2X20 | 40
12 |  | DUMRAON |  |  |  | 132/33 KV | 2X20 | 40
13 |  | BUXUR |  |  |  | 132/33 KV | 2X20 | 40
E | MUZAFFARPUR
1 |  | MUZAFFARPUR |  |  |  | 132/33 KV | 2X50 | 100
2 |  | HAZIPUR 220KV | 220/132 KV | 2X100 | 200
3 |  | HAZIPUR 132 KV |  |  |  | 132/33 KV | 1X50 + 2X20 | 90
4 |  | DARBHANGA 220 KV | 220/132 KV | 2X100 | 200
5 |  | DARBHANGA 132 KV |  |  |  | 132/33 KV | 1X50 + 1X20 | 70
6 |  | GOPALGANJ | 220/132 KV | 2X100 | 200 | 132/33 KV | 2X20 | 40
7 |  | SHEETALPUR |  |  |  | 132/33 KV | 1X20 +1X10 | 30
8 |  | S.K.M.C.H. |  |  |  | 132/33 KV | 2X50 | 100
9 |  | VAISHALI |  |  |  | 132/33 KV | 2X20 | 40
10 |  | CHAPRA |  |  |  | 132/33 KV | 1X50 +1X20 +1X12.5 | 82.5 |  |  |  | 12.5
11 |  | SIWAN |  |  |  | 132/33 KV | 2X20 | 40
12 |  | MASHRAK |  |  |  | 132/33 KV | 2X20 | 40
13 |  | MOTIHARI |  |  |  | 132/33 KV | 2X20 | 40
14 |  | BETIAH |  |  |  | 132/33 KV | 3X20 | 60
15 |  | RAMNAGAR |  |  |  | 132/33 KV | 2X20 | 40
16 |  | RAXAUL |  |  |  | 132/33 KV | 2X20 | 40
17 |  | DHAKA |  |  |  | 132/33 KV | 2X10 | 20
18 |  | SITAMARHI |  |  |  | 132/33 KV | 1X50 +1X20 | 70
19 |  | RUNISAIDPUR |  |  |  | 132/33 KV | 2X20 | 40
20 |  | SAMASTIPUR |  |  |  | 132/33 KV | 1X50 +2X20 | 90
21 |  | DALSINGHSARAI |  |  |  | 132/33 KV | 2X20 | 40
22 |  | PANDAUL |  |  |  | 132/33 KV | 2X20 | 40
23 |  | MADHUBANI |  |  |  | 132/33 KV | 2X20 | 40
24 |  | JAINAGAR |  |  |  | 132/33 KV | 2X10 | 20
25 |  | PHULPARAS |  |  |  | 132/33 KV | 1X20 +1X10 | 30
26 |  | EKMA |  |  |  | 132/33 KV | 2X10 | 20
F | BHAGALPUR
1 |  | SABAUR |  |  |  | 132/33 KV | 2X50 | 100
2 |  | SULTANGANJ |  |  |  | 132/33 KV | 2X20 | 40
3 |  | BANKA |  |  |  | 132/33 KV | 2X20 | 40
4 |  | KAHALGAON |  |  |  | 132/33 KV | 2X20 | 40
5 |  | JAMALPUR |  |  |  | 132/33 KV | 1X50+1X20 | 70
G | PURNIA
1 |  | MADHEPURA | 220/132 KV | 2X100 | 200 | 132/33 KV | 2X20 | 40
2 |  | BEGUSARAI | 220/132 KV | 2X100 | 200 | 132/33 KV | 2X50 | 100
3 |  | B.T.P.S. |  |  |  | 132/33 KV | 1X50 +1X20 | 70
4 |  | PURNIA |  |  |  | 132/33 KV | 2X50 +1X20 | 120
5 |  | KHAGARIA |  |  |  | 132/33 KV | 2X20 | 40
6 |  | NAUGACHIA |  |  |  | 132/33 KV | 2X20 | 40
7 |  | KATIHAR |  |  |  | 132/33 KV | 3X20 | 90
8 |  | SAHARSA |  |  |  | 132/33 KV | 2X20 | 40
9 |  | UDA KISHANGANJ |  |  |  | 132/33 KV | 2X20 | 40
10 |  | SUPAUL |  |  |  | 132/33 KV | 2X10 | 20
11 |  | FARBISHGANJ |  |  |  | 132/33 KV | 2X20 | 40
12 |  | KISHANGANJ |  |  |  | 132/33 KV | 2X20 | 40
13 |  | KATAIYA |  |  |  | 132/33 KV | 3X20 | 60
|  | TOTAL |  | 3250 MVA | 3250 |  | 5332.5 MVA | 5362.5 |  | 109.9 MVA | 109.9

## list of TR (hidden)
POWER TRANSFORMER IN BSPHCL
Sl No. | Name of GSS | Power Transformer Capacity; (in MVA) | [5 empty] | Spare Tr not in use | Tr Circle
|  | 220/132KV |  | 132/33KV |  | 132/25KV
|  | Capacity | Total | Capacity | Total Capacity | Capacity | Total
1 | Jakkanpur |  |  | 3X50+1X20 | 170 |  |  |  | Patna
2 | Khagaul | 3X100 | 300 | 3X50 | 150 |  |  |  | Patna
3 | Digha |  |  | 2X50 | 100 |  |  |  | Patna
4 | Bihta |  |  | 2X50 | 100 |  |  |  | Patna
5 | Mithapur |  |  | 2X50 | 100 |  |  |  | Patna
6 | Karbighaya |  |  | 4X50 | 200 |  |  |  | Patna
7 | Gaighat |  |  | 2X50 | 100 |  |  |  | Patna
8 | Katra |  |  | 2X50 | 100 |  |  |  | Patna
9 | Sipara | 2X150 | 300 | 2X50 | 100 |  |  |  | Patna
10 | Fatuha | 4X100 | 400 | 3X50 | 150 |  |  |  | Patna
11 | Masaudhi |  |  | 2X20 | 40 |  |  |  | Patna
| Net Capacity |  | 1000 |  | 1310
12 | Biharsarif (SG) | 3X50 | 450 | 1X20 | 20 |  |  |  | Biharsarif
13 | Baripahari |  |  | 2X50 | 100 |  |  |  | Biharsarif
14 | Rajgir |  |  | 2X20 | 40 |  |  |  | Biharsarif
15 | Nalanda |  |  | 2X20 | 40 |  |  |  | Biharsarif
16 | Barh |  |  | 1X50+1X20 | 70 |  |  |  | Biharsarif
17 | Hathidah |  |  | 3X20 | 60 |  |  |  | Biharsarif
18 | Shekhpura |  |  | 2X20 | 40 |  |  |  | Biharsarif
19 | Lakhisarai |  |  | 3X20 | 60 |  |  |  | Biharsarif
20 | Jamui |  |  | 2X20 | 40 |  |  |  | Biharsarif
21 | Harnaut |  |  | 2X20 | 40 |  |  |  | Biharsarif
22 | Ekangarsarai |  |  | 2X20 | 40 |  |  |  | Biharsarif
| Net Capacity |  | 450 |  | 550
23 | Chandauti |  |  | 2X50 | 100 | 2X13.35 | 26.7 |  | Gaya
24 | Belaganj |  |  | 2X20 | 40 |  |  | (2X10) | Gaya
25 | Jehanabad |  |  | 2X20 | 40 |  |  |  | Gaya
26 | Ataula |  |  | 2X20 | 40 |  |  |  | Gaya
27 | Bodhgaya | 3X150 | 450 | 2X50 | 100 |  |  |  | Gaya
28 | Sherghati |  |  | 2X20 | 40 |  |  |  | Gaya
29 | Rafiganj |  |  | 2X20 | 40 |  |  |  | Gaya
30 | Nawada |  |  | 1X50+1X20 | 70 |  |  | (1X20) | Gaya
31 | Tekari |  |  | 2X20 | 40 |  |  |  | Gaya
32 | Wajirganj |  |  | 2X20 | 40 |  |  |  | Gaya
33 | Tehta |  |  | 2X20 | 40 |  |  |  | Gaya
34 | Hulasganj |  |  | 2X20 | 40 |  |  |  | Gaya
| Net Capacity |  | 450 |  | 630 |  | 26.7
35 | Dehri | 3X100+1X50 | 350 | 2X50 | 100 |  |  |  | Dehri
36 | Banjari |  |  | 2X20 | 40 |  |  |  | Dehri
37 | Kudra |  |  | 2X20 | 40 |  |  |  | Dehri
38 | Mohania |  |  | 2X20 | 40 |  |  |  | Dehri
39 | Karamnasa |  |  | 1X50+2X20 | 90 | 1X21.6+1X20 | 41.6 |  | Dehri
40 | Sasaram |  |  | 2X20 | 40 |  |  |  | Dehri
41 | Bikramganj |  |  | 2X20 | 40 |  |  |  | Dehri
42 | Sonenagar |  |  | 1X50+1X20+1X10 | 80 | 1X21.6+1X20 | 41.6 |  | Dehri
43 | Aurangabad |  |  | 2X20 | 40 |  |  |  | Dehri
44 | Goh |  |  | 2X20 | 40 |  |  |  | Dehri
45 | Ara |  |  | (1X50+1X20) | 70 |  |  |  | Dehri
46 | Jagdhishpur |  |  | (2X20) | 40 |  |  |  | Dehri
47 | Dumroan |  |  | 2X20 | 40 |  |  |  | Dehri
48 | Buxar |  |  | 2X20 | 40 |  |  |  | Dehri
| Net Capacity |  | 350 |  | 740 |  | 83.2
49 | Muzaffarpur |  |  | 2X50 | 100 |  |  |  | Muzaffarpur
50 | SKMCH |  |  | 2X50 | 100 |  |  |  | Muzaffarpur
51 | Vaishali |  |  | 2X50 | 40 |  |  |  | Muzaffarpur
52 | Hazipur (220KV) | 2X100 | 200 | [5 empty] | Muzaffarpur
53 | Hazipur (132KV) |  |  | 1X50+2X20 | 90 |  |  |  | Muzaffarpur
54 | Jandaha |  |  | 2X20 | 40 |  |  |  | Muzaffarpur
55 | Sheetalpur |  |  | 2X20 | 40 |  |  | (1X10) | Muzaffarpur
56 | Chapra |  |  | 1X50+1X20+1X12.5 | 82.5 |  |  |  | Muzaffarpur
57 | Ekma |  |  | 1X10 | 10 |  |  |  | Muzaffarpur
58 | Siwan |  |  | 1X50+1X20+1X12.5 | 70 |  |  |  | Muzaffarpur
59 | Goplaganj | 2X100 | 200 | 2X20 | 40 |  |  |  | Muzaffarpur
60 | Mushrakh |  |  | 2X20 | 40 |  |  |  | Muzaffarpur
61 | Motihari |  |  | 2X20 | 40 |  |  |  | Muzaffarpur
62 | Bettia |  |  | 2X20 | 40 |  |  |  | Muzaffarpur
63 | Ramnagar |  |  | 2X20 | 40 |  |  |  | Muzaffarpur
64 | Raxaul |  |  | 2X20 | 40 |  |  |  | Muzaffarpur
65 | Dhaka |  |  | 1X20+1X10 | 30 |  |  | (1X10) | Muzaffarpur
66 | Sitamarhi |  |  | 1X50+1X20 | 70 |  |  |  | Muzaffarpur
67 | Runisaidpur |  |  | 2X20 | 40 |  |  |  | Muzaffarpur
68 | Samastipur |  |  | 1X50+2X20 | 90 |  |  |  | Muzaffarpur
69 | Dalsinghsarai |  |  | 2X20 | 40 |  |  |  | Muzaffarpur
70 | Darbhanga (220kV) | 2X100 | 200 | [5 empty] | Muzaffarpur
71 | Darbhanga ( 132KV) |  |  | 1X50+1X20 | 70 |  |  |  | Muzaffarpur
72 | Pandaul |  |  | 2X20 | 40 |  |  |  | Muzaffarpur
73 | Madhubani |  |  | 2X20 | 40 |  |  |  | Muzaffarpur
74 | Jainagar |  |  | 2X10 | 20 |  |  |  | Muzaffarpur
75 | Phoolparas |  |  | 1X20+1X10 | 30 |  |  | (1X10) | Muzaffarpur
| Net Capacity |  | 600 |  | 1282.5
76 | Purnea |  |  | 2X50+1X20 | 120 |  |  |  | Purnea
77 | Khagaria |  |  | 2x20 | 40 |  |  |  | Purnea
78 | Begusarai | 2X100 | 200 | 2X50 | 100 |  |  |  | Purnea
79 | Katihar |  |  | 3X20 | 60 |  |  |  | Purnea
80 | Saharsa |  |  | 2X20 | 40 |  |  |  | Purnea
81 | Udakishanganj |  |  | 2X20 | 40 |  |  |  | Purnea
82 | Sonebarsa |  |  | 2X20 | 40 |  |  |  | Purnea
83 | Supoul |  |  | 1X20 + 1x20 | 40 |  |  | (2X10) | Purnea
84 | Madhepura | 2X100 | 200 | 2X20 | 40 |  |  |  | Purnea
85 | Forbisganj |  |  | 2X20 | 40 |  |  |  | Purnea
86 | Kishanganj |  |  | 2X20 | 40 |  |  |  | Purnea
87 | Kataya, Birpur |  |  | 3X20 | 60 |  |  |  | Purnea
| Net Capacity |  | 400 |  | 660
88 | Sabour |  |  | 2X50 | 100 |  |  |  | Bhagalpur
89 | Sultanganj |  |  | 3X20 | 60 |  |  |  | Bhagalpur
90 | Banka |  |  | 2X20 | 40 |  |  |  | Bhagalpur
91 | Jamalpur |  |  | 1X50+1X20 | 70 |  |  |  | Bhagalpur
92 | Naugachia |  |  | 2X20 | 40 |  |  | (1X20) | Bhagalpur
93 | Kahalgaon |  |  | 2X20 +1X50 | 90 |  |  |  | Bhagalpur
| Net Capacity |  | 0 |  | 400
| Total Capacity |  | 3250 |  | 5572.5 |  | 109.9 |  |  |  | 5482
1 | BTPS |  |  | 1X50+1X20 | 70 | [5 empty] | 90
2 | Pusouli (PG) |  |  | 1X10 | 10 |  |  |  |  | 5572.5
3 | Balmikinagar |  |  | 1X10 | 10
| Grand__Total |  |  |  | 5662.5
Gaya

## 132kv line (hidden)
BSPTCL 132 KV TRANSMISSION LINES
Sl. No | Name of Line | Circuit | Ckt Km Length | Total length (in Km) | Conductor type and characteristics
1 | 132 KV Bodhgaya-Chandauti (Line-I) | Double | 16 | 32 | Panther
2 | 132 KV Bodhgaya-Chandauti (Line-II) | Double | 14 | 28 | Panther
3 | 132 KV Chandauti-Sipara | Double | 90 | 90 | Panther
4 | 132KV Gaya-Tehta | Single | 6 | 6 | Panther
5 | 132KV Tehta-Belaganj | Single | 22 | 22 | Panther | commisioned on 20-02-14
6 | 132KVBelaganj-Jehanabad | Single | 30 | 30 | Panther
7 | 132KV Jehanabad-Masaudhi | Single | 30 | 30 | Panther
8 | 132KV Masaudhi-Sipara | Single | 24 | 24 | Panther
9 | 132KV Jehanabad-Ataula | Single | 28 | 28 | Panther
10 | 132KV Chandauti-Sonenagar (L-30) | Single | 76 | 76 | Panther
11 | 132KV Chandauti-Rafiganj (L-31) | Single | 41 | 41 | Panther
12 | 132KV Rafiganj-Sonenagar (L-31) | Single | 35 | 35 | Panther
13 | 132KV Sonenagar-Rihand | Single | 188 | 188 | Panther
14 | 132KV Sonenagar-Japla-Garhwa-Rihand | Single | 188 | 188 | Panther
15 | 132KV Chandauti-Tekari | Single | 28.9 | 28.9 | Panther
16 | 132KV Tekari-Goh | Single | 22 | 22 | Panther
17 | 132KV Bodhgaya-Wazirganj | Single | 30 | 30 | Panther
18 | 132KV Wazirganj-Nawada | Single | 26 | 26 | Panther
19 | 132KV Bodhgaya-Sherghati | Single | 27 | 27 | Panther
20 | 132KV Bodhgaya-Sherghati-Imamganj | Single | 30.04 | 30.04 | Panther
21 | 132KV Dehri-Banjari | Single | 38 | 38 | Panther
22 | 132KV Banjari-KCL | Single | 1 | 1 | Panther
23 | 132KV Dehri-Sasaram ckt-I | Single | 20 | 20 | Panther
24 | 132KV Sasaram-Banjari | Singal | 47.5 | 47.5 | Panther
24 | 132KV Sasaram-kudra Ckt-I | Single | 13 | 13 | Panther
25 | 132KV Kudra-Karamnasa Ckt-I | Single | 10 | 10 | Panther
26 | 132KV Dehari-Pusouli Ckt-II | Single | 26 | 26 | Panther
27 | 132KV Dehri-Kudra | Double | 2 | 4 | Panther
28 | 132KV Pusouli-Mohania Ckt-II | Single | 10 | 10 | Panther
29 | 132KV Mohania Karamnasa Ckt-II | Single | 11 | 11 | Panther
30 | 132KV Karamnasa-Sahupuri | Single | 131 | 131 | Panther
31 | 132KV Karamnasa-Chandauli-Sahupuri | Single | 131 | 131 | Panther
32 | 132KV Dehri-Bikramganj Ckt-II | Single | 45 | 45 | Panther
33 | 132KV Bikramganj-Dumraon Ckt-II | Single | 35 | 35 | Panther
34 | 132KV Dehri-Dumroan Ckt-I | Single | 80 | 80 | Panther
35 | 132KV Dumroan-Buxar | Single | 16.1 | 16.1 | Panther
36 | 132KV Sonenagar Aurangabad | Single | 21 | 21 | Panther
| 132KV Aurangabad-Shree Cement | Single | 0.75 | 0.75 | Panther
36 | 132KV Dehri-Sonenagar | Double | 14.45 | 28.9 | Panther
37 | 132KV Ara (PG)-Ara | Single | 7 | 7 | Panther
38 | 132KV Ara (PG)-Dumroan | Single | 60 | 60 | Panther
39 | 132KV Ara (PG)-Jagdishpur | Single | 26.3 | 26.3 | Panther
40 | 132KV Fatuha-Sipara | Single | 26 | 26 | Panther
41 | 132KV Sipara- Mithapur | Single | 16 | 16 | Panther
42 | 132kV Mithapur-Jakkanpur | Single | 1 | 1 | Panther
43 | 132KV Mithapur-Karbighaia | Double | 2.47 | 4.94 | Panther
44 | 132KV Fatuha-Gaighat | Single | 23 | 23 | Panther
45 | 132KV Fatuah-Katra | Single | 17 | 17 | Panther
46 | 132KV Katra-Gaighat | Single | 15 | 15 | Panther
47 | 132KV Khagaul-Bihta | Double | 14.5 | 29 | Panther
48 | 132KV Khagaul-Digha | Double | 16 | 32 | Panther
49 | 132KV Biharsarif (SG)-Baripahari | Double | 5 | 10 | Panther
50 | 132KV Biharsarif (SG)-Barh Ckt-I | Single | 25 | 25 | Panther
51 | 132KV Barh-Hathidah Ckt-I | Single | 20 | 20 | Panther
52 | 132KV Biharsarif (SG)-Hathidah Ckt-II | Single | 32.5 | 32.5 | Panther
53 | 132KV Biharsarif (SG)-Ekangarsarai | Single | 30 | 30 | Panther
54 | 132KV Ekangarsarai-Hulasganj | Single | 14.5 | 14.5 | Panther
55 | 132KV Baripahari-Harnaut | Single | 26 | 26 | Panther
56 | 132KVHarnaut-Fatuha | Single | 45 | 45 | Panther
57 | 132KV Biharsarif (SG)-Barhi (DVC)(L-28) | Single | 142 | 142 | Panther
58 | 132KV Nalanda-(L-28)LILO | Double | 2 | 4 | Panther
59 | 132KV(L -28) Line-Rajigir grid (t-connection) | Single | 6 | 6 | Panther
60 | 132KVBarhi (DVC)-Rajgir (L-29) | Single | 16 | 16 | Panther
61 | 132KVRajgir-Biharsarif (L-29) | Single | 126 | 126 | Panther
62 | 132KV Biharsarif (SG)-Nawada | Single | 41 | 41 | Panther
63 | 132KV Hathidah-Lakhisarai | Single | 28 | 28 | Panther
64 | 132KV Hathidah-Shehpura | Single | 28 | 28 | Panther
65 | 132KV Lakhisarai-Jamui | Single | 35 | 35 | Panther
66 | 132KV Biharsarif (SG)-Shekhpura | Single | 39.49 | 39.49 | Panther
67 | 132KV Shekhpura-Jamui | Single | 49 | 49 | Panther
68 | 132KV Lakhisarai-Jamalpur | Single | 45 | 45 | Panther
69 | 132KV Sultanganj-Jamalpur | Single | 38 | 38 | Panther
70 | 132KV Ara-Ara TSS | Single | 4.01 | 4.01 | Panther
71 | 132KV Dumroan-Dumroan TSS | Single | 2 | 2 | Panther
72 | 132KV Bodhgaya-Paharpur TSS | Double | 35 | 70 | Panther
73 | 132KV Rafiganj-Rafiganj TSS | Single | 4.6 | 4.6 | Panther
74 | 132KV Barh/Hathidah line-Mokama TSS | Single | 6 | 6 | Panther
75 | 132KV Lakhisarai - Lakhisarai TSS | Single | 6 | 6 | Panther
76 | 132KV Jamui-Jhajha TSS | Double | 31 | 62 | Panther
77 | 132KV Khagaul-Khagaul TSS | Single | 1 | 1 | Panther
78 | 132KV Fatuha-Khusrupur TSS | Single | 7.2 | 7.2 | Panther
79 | 132KV Sabour-Sultanganj Ckt-I | Single | 30 | 30 | Panther
80 | 132KV Sabour-Sultanganj Ckt-II | Single | 31 | 31 | Panther
81 | 132KV Sultanganj-Deoghar | Single | 105 | 105 | Panther
82 | 132KV KhSTSPS-Sabour | Single | 25 | 25 | Panther
83 | 132KV KhSTPS Kahalgaon | Single | 6 | 6 | Panther
84 | 132KV Sabour-Kahalgaon | Single | 19 | 19 | Panther
85 | 132KV Kahalgaon- Lalmatia | Single | 60 | 60 | Panther
86 | 132KV Banka (PG)-Sabour | Single | 41.58 | 41.58 | Panther
87 | 132KV Banka (PG)-Banka | Single | 10 | 10 | Panther
88 | 132KV Purnea (PG)-Purnea | Triple | 1.33 | 3.99 | Panther
89 | 132KV Purnea-Naugachia (L-16) | Single | 70 | 70 | Panther
90 | 132KV Naugachia-BTPS (L-16) | Single | 136 | 136 | Panther
91 | 132KV Purnea-Khagaria (L-23) | Single | 150 | 150 | Panther
92 | 132KV Khagaria-BTPS (L-23) | Single | 60 | 60 | Panther
93 | 132KV Purnea-Katihar | Single | 29 | 29 | Panther
94 | 132KV Purnea-Saharsa | Single | 101.2 | 101.2 | Panther
95 | 132KV Purnea-Forbishganj | Single | 85 | 85 | Panther
96 | 132KV Purnea (PG)-Kishanganj | Single | 70 | 70 | Panther
97 | 132KV Dalkola (WB)-Kishanganj | Single | 26 | 26 | Panther
98 | 132KV Kishanganj-Forbisganj | Single | 88.6 | 88.6 | Panther
99 | 132KV Forbisganj-Kataya Ckt-I | Single | 39.7 | 39.7 | Panther
100 | 132KV Farbisganj-Kataya Ckt-II (old) | Single | 50.9 | 50.9 | Panther
101 | 132KV Madhepura-Saharsa | Single | 50 | 50 | Panther
102 | 132KV Madhepura-Sonebarsa | Single | 50 | 50 | Panther
103 | 132KV Madhepura-Supoul | Double | 30 | 60 | Panther
104 | 132KV Saharsa-Uda Kishanganj | Single | 50.35 | 50.35 | Panther
105 | 132KV Supoul-Kataya | Double | 59.6 | 119.2 | Panther
106 | 132KV BTPS-Begusarai (L-9 & L-10) | Double | 10 | 20 | Panther
107 | 132KV Begusarai-Samastipur (L-9) | Single | 57 | 57 | Panther
108 | 132KV Begusarai-Dalsingsarai (L-10) | Single | 34 | 34 | Panther
109 | 132KV Begusarai-Kuseswarstan | Single | 65.54 | 65.54 | Panther
110 | 132KV Dalsingsarai-Samastipur (L-10) | Single | 23 | 23 | Panther
111 | 132KV KBUNL-Samastipur | Double | 85.2 | 170.4 | Panther
112 | 132KV KBUNL-Muzaffarpur Ckt-I | Single | 15.5 | 15.5 | Panther
113 | 132KV KBUNL-Muzaffarpur Ckt-II | Single | 16.7 | 16.7 | Panther
| 132KV Muzaffarpur-SKMCH | Single | 16.7 | 16.7 | Panther
114 | 132KV KBUNL-SKMCH | Single | 14.116 | 14.116 | Panther
115 | 132KV Samastipur -Darbhanga | Single | 40 | 40 | Panther
116 | 132KVSamastipur- Hazipur | Single | 70 | 70 | Panther
117 | 132KV Hajipur - Jandaha | Single | 48 | 48 | Panther | 20.03.14
118 | 132KV Jandaha - Samastipur | Single | 44 | 44 | Panther | 20.03.14
119 | 132KV Hazipur (220KV) - Hazipur (132KV) | Double | 2 | 4 | Panther
120 | 132KV Hazipur- Sheetalpur | Single | 30 | 30 | Panther
121 | 132KV Chapra- Sheetalpur | Single | 40 | 40 | Panther
122 | 132KV Muzaffarpur- Vaishali | Single | 30.1 | 30.1 | Panther
123 | 132KV Vaishali-Sheetalpur | Double | 30.21 | 60.42 | Panther
124 | 132KV Chapra - Siwan | Single | 70 | 70 | Panther
125 | 132KV Chapra/Siwan - Ekma | Single | 0.6 | 0.6 | Panther
126 | 132KV Gopalganj - Siwan | Single | 40 | 40 | Panther
127 | 132KV Gopalganj - Musrakh- Siwan | Single | 74.866 | 74.866 | Panther
128 | 132KV Gopalganj - Bettia | Double | 60.75 | 121.5 | Panther
129 | 132KV Gopalganj/ Bettia Ckt-1- Sidhwalia SM | Single | 12 | 12 | Panther
130 | 132KV MTPS - Motihari | Single | 70 | 70 | Panther
131 | 132KV Bettia - Motihari | Single | 45 | 45 | Panther
132 | 132KV Bettia - Ramnagar | Single | 41.5 | 41.5 | Panther
133 | 132KV Bettia - Raxaul | Single | 37.1 | 37.1 | Panther
134 | 132KV Ramnagar - BHPC, Balmikinagar | Single | 77.77 | 77.77 | Panther
135 | 132KV Motihari - Dhaka | Single | 24 | 24 | Panther
136 | 132KV Dhaka - Sitamarhi | Single | 52 | 52 | Panther
137 | 132KV Sitamarhi - Runisaidpur | Single | 21 | 21 | Panther
138 | 132KV Runisaidpur - SKMCH | Single | 35 | 35 | Panther
139 | 132KV SKMCH- Muzaffarpur | Single | 15 | 15 | Panther
140 | 132KV Darbhanga (220KV) - Darbhanga (132KV) | Single | 1 | 1 | Panther
141 | 132 KV Darbhanga - Phoolparas | Single | 71.8 | 71.8 | Panther
142 | 132KV Darbhanga - Pandaul | Single | 28 | 28 | Panther
143 | 132KV Pandaul - Madhubani | Single | 16 | 16 | Panther
144 | 132KV Maadhubani - Jainagar | Single | 40 | 40 | Panther |  |  | Single
145 | 132KV Jainagar - Phoolparas | Single | 55 | 55 | Panther
146 | 132KV Phoolparas - Supoul | Double | 31.92 | 63.84 | Panther
147 | 132KV Chapra - Chapra TSS | Single | 1 | 1 | Panther
148 | 132KV Hazipur - Hazipur TSS | Single | 2 | 2 | Panther
149 | 132KV Sonenagar-Aurangabad | Single | 21 | 21 | Panther |  | 6006.172
Total Length of 132KV Transmission Line |  |  |  | 6264.702
Total Number of Lines=174

## 220kv line (hidden)
Bihar State Power Transmission Company Ltd.
BSPTCL 220KV TRANMISSION LINES
Sl. No | Name of Line | Circuit | Ckt Km Length | Total length (in Km) | Conductor type and characteristics | No Sub-Conductor (NSC)
1 | 220KV Biharsarif (PG) - Biharsarif | Triple | 1.67 | 5.01 | Zebra | Single
2 | 220KV Biharsarif - Bodhgaya | Double | 80 | 160 | Zebra | Single
3 | 220KV Biharsarif - Fathua | Double | 40 | 80 | Zebra | Single
4 | 220KV Biharsarif - Begusarai | Double | 75 | 150 | Zebra | Single
5 | 220KV Begusarai- MTPS | Double | 152 | 304 | Zebra | Single
6 | 220KV Gaya (PG) - Bodhgaya | Double | 17 | 34 | Zebra | Single
7 | 220KV Gaya (PG) - Dehri | Double | 95 | 190 | Zebra | Single
8 | 220KV Pusouli - Dehri | Single | 65 | 65 | Zebra | Single
9 | 220KV Pusouli - Sahupuri (UP) | Single | 71 | 71 | Zebra | Single
10 | 220KV Patna (PG ) - Sipara | Double | 0.45 | 0.9 | Zebra | Single
11 | 220KV Patna (PG) - Fatuha | Single | 26 | 26 | Zebra | Single
12 | 220 KV Sipara - Fatuha | Single | 26 | 26 | Zebra | Single
13 | 220 KV Patna (PG) - Khagaul | Single | 40 | 40 | Zebra | Single
14 | 220KV Sipara - Khagaul | Single | 39 | 39 | Zebra | Single
15 | 220KV KBUNL - Gopalganj | Single | 101.35 | 101.35 | Zebra | Single
16 | 220KV KBUNL - Darbhanga | Single | 68.53 | 68.53 | Zebra | Single
17 | 220KV Biharsarif - TTPS | Single | 225 | 225 | Moose | Double
18 | 220KV Purnea (PG) - Madhepura | Double | 100.09 | 200.18 | Zebra | Single
19 | 220KV Muzaffarpur (PG) - Hazipur | Double | 51 | 102 | Zebra | Single
20 | 220KV MTPS-Kafen | Double | 24 | 48 | Zebra | Single
Total Length of 220 KV Tr. Line |  |  |  | 1935.97
Total Number of Lines=32

## 220kv cal
BSPTCL 220 KV TRANSMISSION LINES (As on 30.09.18)
Line ID | Sl. No | Name of Line | Circuit | Ckt Km Length | Total length (in Km) | Conductor type and characteristics | No Sub-Conductor (NSC) | SIL | Wi ckt | Ckts | Wi | Ti | TNAi | Wi(Ti-Tnai)/Ti
SBPDCL
2B1 | 1 | 220KV Biharsarif (PG) - Biharsarif | Triple | 1.67 | 5.01 | Zebra | Single | 132 | 220.44 | 3 | 661.32 | 2160 | 0 | 661.32
2BG1 | 2 | 220KV Biharsarif - Khizisarai(BGCL) | Double | 97 | 194 | Zebra | Single | 132 | 12804 | 2 | 25608 | 1440 | 0 | 25608
2G2 | 3 | 220KV Khizisarai(BGCL) - Bodhgaya | Double | 58 | 116 | Zebra | Single | 132 | 7656 | 2 | 15312 | 1440 | 0 | 15312
2BP1 | 4 | 220KV Biharsarif - Fathua | Double | 40 | 80 | Zebra | Single | 132 | 5280 | 2 | 10560 | 1440 | 24.7333 | 10378.6222
2G1 | 5 | 220KV Gaya (PG) - Bodhgaya | Double | 17 | 34 | Zebra | Single | 132 | 2244 | 2 | 4488 | 1440 | 0 | 4488
2DG1 | 6 | 220KV Gaya (PG) - Dehri | Double | 95 | 190 | Zebra | Single | 132 | 12540 | 2 | 25080 | 1440 | 0 | 25080
2D1 | 7 | 220KV Pusouli - Dehri | Single | 65 | 65 | Zebra | Single | 132 | 8580 | 1 | 8580 | 720 | 0 | 8580
2D2 | 8 | 220KV Pusouli - Sahupuri (UP) | Single | 71 | 71 | Zebra | Single | 132 | 9372 | 1 | 9372 | 720 | 1.5167 | 9352.2581
2P1 | 9 | 220KV Patna (PG ) - Sipara | Double | 0.45 | 0.9 | Zebra | Single | 132 | 59.4 | 2 | 118.8 | 1440 | 0 | 118.8
2P2 | 10 | 220KV Patna (PG) - Fatuha | Single | 26 | 26 | Zebra | Single | 132 | 3432 | 1 | 3432 | 720 | 11.9333 | 3375.1178
2P3 | 11 | 220 KV Sipara - Fatuha | Single | 26 | 26 | Zebra | Single | 132 | 3432 | 1 | 3432 | 720 | 16.85 | 3351.6817
2P4 | 12 | 220 KV Patna (PG) - Khagaul | Single | 40 | 40 | Zebra | Single | 132 | 5280 | 1 | 5280 | 720 | 0.58333 | 5275.7222
2P5 | 13 | 220KV Sipara - Khagaul | Single | 39 | 39 | Zebra | Single | 132 | 5148 | 1 | 5148 | 720 | 0.58333 | 5143.8292
2B2 | 14 | 220KV Biharsarif - TTPS | Single | 73 | 73 | Moose | Double | 515 | 37595 | 1 | 37595 | 720 | 0 | 37595
2DG2 | 15 | 220KV Gaya(PG)- Sonenagar | Double | 91.591 | 183.182 | Zebra | Single | 132 | 12090.012 | 2 | 24180.024 | 1440 | 0 | 24180.024
2D3 | 16 | 220KV LILO Pusouli-(220 KV Pusoli(PG)-Ara(PG) ckt-2) | Double | 4.57 | 9.14 | Zebra | Single | 132 | 603.24 | 2 | 1206.48 | 1440 | 4 | 1203.1287
2P6 | 17 | 220KV Patna (PG ) - Sipara ckt-3 | Single | 0.3 | 0.3 | Zebra | Single | 132 | 39.6 | 1 | 39.6 | 720 | 0 | 39.6 |  | 1152.532
2G4 | 18 | 220 kV Gaya(PG)- Khizisarai D/C | Double | 51.69 | 103.38 | Zebra | Single | 132 | 6823.08 | 2 | 13646.16 | 1440 | 0 | 13646.16
| Total Length of 220 KV Tr. Line SB - |  |  |  | 1255.912 |  |  |  |  | 29 | 193739.384 | 20880 | 60.2 | 193389.2638 |  | 110.36
|  | TOTAL NUMBR OF LINES FOR SBPDCL = 29 | [6 empty] | SBPDCL Avo= |  |  | 0.99819
2G3 |  | 220KV Khigisarai-220/132/33KV GIS Nawada | Double | 55.18 | 110.36 | HTLS | UNDER BGCL
|  | 220KV Jamalpur(New)-Sabour(New) | Double | 60 | 120 | Zebra | Under BGCL
NBPDCL
Line ID | Sl. No | Name of Line | Circuit | Ckt Km Length | Total length (in Km) | Conductor type and characteristics | No Sub-Conductor (NSC) | SIL | Wi ckt | Ckts | Wi | Ti | TNAi | Wi(Ti-Tnai)/Ti
2N1 | 1 | 220KV BTPS - Begusarai | Single | 15 | 15 | Zebra | Single | 132 | 1980 | 1 | 1980 | 720 | 0 | 1980
2BN1 | 2 | 220KV Biharsarif - BTPS | Single | 60 | 60 | Zebra | Single | 132 | 7920 | 1 | 7920 | 720 | 0 | 7920
2BN2 | 3 | 220KV Biharsarif - Begusarai | Single | 75 | 75 | Zebra | Single | 132 | 9900 | 1 | 9900 | 720 | 6.8167 | 9806.2708
2M1 | 4 | 220kV MTPS-Samastipur(New)(LILO at loc. 241) | Double | 82.5 | 165 | Zebra | Single | 132 | 10890 | 2 | 21780 | 1440 | 5.6667 | 21694.2917
2MN1 | 5 | 220 kV Samastipur(New)-Begusarai(LILO at loc. 239) | Double | 55 | 110 | Zebra | Single | 132 | 7260 | 2 | 14520 | 1440 | 21.4 | 14304.2167
2M2 | 6 | 220KV MTPS - Gopalganj | Double | 101.35 | 202.7 | Zebra | Single | 132 | 13378.2 | 2 | 26756.4 | 1440 | 6.05 | 26643.986
2M3 | 7 | 220KV MTPS - Motipur | Double | 37.8 | 75.6 | Zebra | Single | 132 | 4989.6 | 2 | 9979.2 | 1440 | 0 | 9979.2
2M4 | 8 | 220KV Motipur-Mushahri ckt-I | Single | 88.732 | 88.732 | Zebra | Single | 132 | 11712.624 | 1 | 11712.624 | 720 | 18.3167 | 11414.657
2M5 | 9 | 220KV Motipur-Mushahri ckt-II | Single | 84.032 | 84.032 | Zebra | Single | 132 | 11092.224 | 1 | 11092.224 | 720 | 2.8667 | 11048.0605
2M6 | 10 | 220KV Mushahri - Darbhanga ckt-I | Single | 57.868 | 57.868 | Zebra | Single | 132 | 7638.576 | 1 | 7638.576 | 720 | 0 | 7638.576
2M7 | 11 | 220KV Mushahri - Darbhanga ckt-II | Single | 53.168 | 53.168 | Zebra | Single | 132 | 7018.176 | 1 | 7018.176 | 720 | 0 | 7018.176
2N2 | 12 | 220KV Purnea (PG) - Madhepura | Double | 100.09 | 200.18 | Zebra | Single | 132 | 13211.88 | 2 | 26423.76 | 1440 | 19.2167 | 26071.1374
2M8 | 13 | 220KV Muzaffarpur (PG) - Hazipur | Double | 51 | 102 | Zebra | Single | 132 | 6732 | 2 | 13464 | 1440 | 21.3333 | 13264.5333
2N3 | 14 | 220 kV Kishanganj (PG)- Kishanganj (New) | Double | 4.236 | 8.472 | L/59 | - | 132 | 559.152 | 2 | 1118.304 | 1440 | 0 | 1118.304
2M9 | 15 | 220KV MTPS-Kafen | Double | 24 | 48 | Zebra | Single | 132 | 3168 | 2 | 6336 | 1440 | 0 | 6336
2M10 | 16 | 220 kV Samastipur(New)-Darbhanga(400/220) | Single | 48 | 48 | Zebra | Single | 132 | 6336 | 1 | 6336 | 720 | 0 | 6336
2M12 | 17 | 220 kV Motipur- DMTCL | Double | 109 | 218 | Zebra | Single | 132 | 14388 | 2 | 28776 | 1440 | 10.05 | 28575.1675
2M13 | 18 | 220 kV Darbhanga(DMTCL)- Laukahi | Double | 88.8 | 177.6 | Zebra | Single | 132 | 11721.6 | 2 | 23443.2 | 1440 | 19.4 | 23127.368
2M14 | 19 | 220KV Madhepura- Laukahi | Double | 62 | 124 | AL/59 | Single | 132 | 8184 | 2 | 16368 | 1440 | 0 | 16368
2M15 | 20 | 220 kV Darbhanga(DMTCL)- Darbhanga ckt-I | Double | 2.92 | 5.84 | Zebra | Single | 132 | 385.44 | 2 | 770.88 | 1440 | 0 | 770.88
2N4 | 21 | 220 KV Purnea(PG)-Begusarai ckt-2 | Single | 189 | 189 | Zebra | Single | 132 | 24948 | 1 | 24948 | 720 | 0 | 24948
2M15 | 22 | 220 kV BTPS-Hajipur | Single | 107 | 107 | Zebra | Single | 132 | 14124 | 1 | 14124 | 720 | 0 | 14124
2MN3 | 23 | 220 kV Kishanganj (New)-Madhepura | Double | 140 | 280 | AL/59 | Single | 132 | 18480 | 2 | 36960 | 1440 | 0 | 36960
| Total Length of 220 KV Tr. Line NBPDCL - |  |  |  | 2495.192 |  |  |  |  | 36 | 329365.344 | 25920 | 131.1167 | 327446.8249
| TOTAL NUMBER OF LINES FOR NBPDCL = 36 | [8 empty] | NBPDCL Avo= |  | 0.99418
2M11 | 21 | 220 kV Hajipur(New)-Chapra(new) | Double | 47.8 | 95.6 | Zebra | Under BGCL | [7 empty] | 4077.064
| Total Length of 220 KV Tr. Line for BSPTCL - |  |  |  | 3751.104 |  |  |  | TOTAL | 65 | 523104.728 |  |  | 520836.0886
| TOTAL NUMBER OF LINES FOR BSPTCL = 65 | [7 empty] | 220TL Total Avo= |  |  | 0.99566

## 132kvv cal
BSPTCL 132 KV TRANSMISSION LINES(As on 30.09.18)
Line ID | Sl. No | Name of Line | Circuit | Ckt Km Length | Total length (in Km) | Conductor type | SIL | Wi ckt | Ckts | Wi | Ti | TNAi | Wi(Ti-Tnai)/Ti
SBPDCL
G1 | 1 | 132 KV Bodhgaya-Chandauti (Line-I) | Double | 16 | 32 | Panther | 50 | 800 | 2 | 1600 | 1440 | 2.6167 | 1597.0926
G2 | 2 | 132 KV Bodhgaya-Chandauti (Line-II) | Double | 14 | 28 | Panther | 50 | 700 | 2 | 1400 | 1440 | 2.0667 | 1397.9907
GP1 | 3 | 132 KV Chandauti-Sipara | Single | 90 | 90 | Panther | 50 | 4500 | 1 | 4500 | 720 | 9.45 | 4440.9375
G3 | 4 | 132KV Gaya-Tehta (LILO) | Single | 6 | 6 | Panther | 50 | 300 | 1 | 300 | 720 | 0 | 300
G4 | 5 | 132KV Tehta-Belaganj (LILO) | Single | 22 | 22 | Panther | 50 | 1100 | 1 | 1100 | 720 | 0 | 1100
G5 | 6 | 132KVBelaganj-Jehanabad (LILO) | Single | 30 | 30 | Panther | 50 | 1500 | 1 | 1500 | 720 | 0 | 1500
GP2 | 7 | 132KV Jehanabad-Masaudhi | Single | 30 | 30 | Panther | 50 | 1500 | 1 | 1500 | 720 | 6.45 | 1486.5625
P1 | 8 | 132KV Masaudhi-Sipara | Single | 24 | 24 | Panther | 50 | 1200 | 1 | 1200 | 720 | 0 | 1200
G6 | 9 | 132KV Jehanabad-Ataula | Double | 28 | 56 | Panther | 50 | 1400 | 2 | 2800 | 1440 | 0 | 2800
DG1 | 10 | 132KV Chandauti-Sonenagar (L-30) | Single | 76 | 76 | Panther | 50 | 3800 | 1 | 3800 | 720 | 3.6667 | 3780.6481
G7 | 11 | 132KV Chandauti-Rafiganj (L-31) | Single | 41 | 41 | Panther | 50 | 2050 | 1 | 2050 | 720 | 0 | 2050
DG2 | 12 | 132KV Rafiganj-Sonenagar (L-31) | Single | 35 | 35 | Panther | 50 | 1750 | 1 | 1750 | 720 | 0 | 1750
D1 | 13 | 132KV Sonenagar-Rihand Ckt-1 | Single | 188 | 188 | Panther | 50 | 9400 | 1 | 9400 | 720 | 148.1667 | 7465.6019
D2 | 14 | 132KV Sonenagar-Japla-Garhwa-Rihand ckt-2 | Single | 188 | 188 | Panther | 50 | 9400 | 1 | 9400 | 720 | 0.6 | 9392.1667
G8 | 15 | 132KV Chandauti-Tekari | Single | 28.9 | 28.9 | Panther | 50 | 1445 | 1 | 1445 | 720 | 0 | 1445
DG3 | 16 | 132KV Tekari-Goh | Single | 22 | 22 | Panther | 50 | 1100 | 1 | 1100 | 720 | 0 | 1100
G9 | 17 | 132KV Bodhgaya-Khizirsarai(BGCL) | Single | 38 | 38 | Panther | 50 | 1900 | 1 | 1900 | 720 | 0 | 1900
G10 | 18 | 132KV Wazirganj-Nawada | Single | 26 | 26 | Panther | 50 | 1300 | 1 | 1300 | 720 | 0 | 1300
G11 | 19 | 132KV Bodhgaya-Sherghati | Single | 27 | 27 | Panther | 50 | 1350 | 1 | 1350 | 720 | 0 | 1350
G12 | 20 | 132KV Bodhgaya-Imamganj | Single | 56 | 56 | Panther | 50 | 2800 | 1 | 2800 | 720 | 0 | 2800
D3 | 21 | 132KV Dehri-Banjari | Single | 38 | 38 | Panther | 50 | 1900 | 1 | 1900 | 720 | 6.6833 | 1882.3634
D4 | 22 | 132KV Banjari-KCL | Single | 1 | 1 | Panther | 50 | 50 | 1 | 50 | 720 | 0 | 50
D5 | 23 | 132KV Dehri-Sasaram ckt-I | Single | 20 | 20 | Panther | 50 | 1000 | 1 | 1000 | 720 | 0 | 1000
D6 | 24 | 132KV Sasaram-Banjari | Single | 47.5 | 47.5 | Panther | 50 | 2375 | 1 | 2375 | 720 | 5.25 | 2357.6823
D7 | 25 | 132KV Sasaram-Kudra Ckt-I | Single | 13 | 13 | Panther | 50 | 650 | 1 | 650 | 720 | 0 | 650
D8 | 26 | 132KV Kudra-Karamnasa Ckt-I | Single | 10 | 10 | Panther | 50 | 500 | 1 | 500 | 720 | 0 | 500
D9 | 27 | 132KV Dehri-Pusouli Ckt-II | Single | 26 | 26 | Panther | 50 | 1300 | 1 | 1300 | 720 | 0 | 1300
D10 | 28 | 132KV Dehri-PSL CKT 2 LILO to Kudra GSS | Double | 2 | 4 | Panther | 50 | 100 | 2 | 200 | 1440 | 0 | 200
D11 | 29 | 132KV Pusouli-Mohania Ckt-II | Single | 10 | 10 | Panther | 50 | 500 | 1 | 500 | 720 | 9.0667 | 493.7037
D12 | 30 | 132KV Mohania Karamnasa Ckt-II | Single | 11 | 11 | Panther | 50 | 550 | 1 | 550 | 720 | 0 | 550
D13 | 31 | 132KV Karamnasa-Sahupuri | Single | 131 | 131 | Panther | 50 | 6550 | 1 | 6550 | 720 | 0 | 6550
D14 | 32 | 132KV Karamnasa-Chandauli-Sahupuri | Single | 131 | 131 | Panther | 50 | 6550 | 1 | 6550 | 720 | 0 | 6550
D15 | 33 | 132KV Dehri-Bikramganj Ckt-II | Single | 45 | 45 | Panther | 50 | 2250 | 1 | 2250 | 720 | 0 | 2250
D16 | 34 | 132KV Bikramganj-Dumraon Ckt-II | Single | 35 | 35 | Panther | 50 | 1750 | 1 | 1750 | 720 | 0 | 1750
D17 | 35 | 132KV Dehri-Kochas(LILO) | Single | 87.6 | 87.6 | Panther | 50 | 4380 | 1 | 4380 | 720 | 0 | 4380
D18 | 36 | 132KV Kochas-Dumroan(LILO) | Single | 55.6 | 55.6 | Panther | 50 | 2780 | 1 | 2780 | 720 | 0 | 2780
D19 | 37 | 132KV Dumroan-Buxar | Double | 16.1 | 32.2 | Panther | 50 | 805 | 2 | 1610 | 1440 | 0 | 1610
D20 | 38 | 132KV Sonenagar -Aurangabad | Double | 21 | 42 | Panther | 50 | 1050 | 2 | 2100 | 1440 | 0 | 2100
D21 | 39 | 132KV Aurangabad-Shree Cement | Single | 0.75 | 0.75 | Panther | 50 | 37.5 | 1 | 37.5 | 720 | 0 | 37.5
D22 | 40 | 132KV Dehri-Sonenagar | Double | 14.45 | 28.9 | Panther | 50 | 722.5 | 2 | 1445 | 1440 | 0 | 1445
D23 | 41 | 132KV Ara (PG)-Ara | Single | 7 | 7 | Panther | 50 | 350 | 1 | 350 | 720 | 0 | 350
D24 | 42 | 132KV Ara (PG)-Dumroan | Single | 60 | 60 | Panther | 50 | 3000 | 1 | 3000 | 720 | 0 | 3000
D25 | 43 | 132KV Ara (PG)-Jagdishpur Ckt-I | Single | 26.3 | 26.3 | Panther | 50 | 1315 | 1 | 1315 | 720 | 0 | 1315
D26 | 44 | 132KV Ara (PG)-Jagdishpur ckt-II | Single | 26 | 26 | Panther | 50 | 1300 | 1 | 1300 | 720 | 0 | 1300
P2 | 45 | 132KV Fatuha-Sipara | Single | 26 | 26 | Panther | 50 | 1300 | 1 | 1300 | 720 | 0 | 1300
P3 | 46 | 132KV Sipara- Mithapur | Single | 16 | 16 | Panther | 50 | 800 | 1 | 800 | 720 | 0 | 800
P4 | 47 | 132kV Mithapur-Jakkanpur | Single | 1 | 1 | Panther | 50 | 50 | 1 | 50 | 720 | 0 | 50
P5 | 48 | 132KV Mithapur-Karbighaia | Double | 2.47 | 4.94 | Panther | 50 | 123.5 | 2 | 247 | 1440 | 0 | 247
P6 | 49 | 132KV Fatuha-Gaighat | Single | 23 | 23 | Panther | 50 | 1150 | 1 | 1150 | 720 | 7.65 | 1137.7812
P7 | 50 | 132KV Fatuah-Katra | Single | 17 | 17 | Panther | 50 | 850 | 1 | 850 | 720 | 0 | 850
P8 | 51 | 132KV Katra-Gaighat | Single | 15 | 15 | Panther | 50 | 750 | 1 | 750 | 720 | 0 | 750
P9 | 52 | 132KV Khagaul-Bihta | Double | 14.5 | 29 | Panther | 50 | 725 | 2 | 1450 | 1440 | 0 | 1450
P10 | 53 | 132KV Khagaul-Digha | Double | 16 | 32 | Panther | 50 | 800 | 2 | 1600 | 1440 | 0 | 1600
B1 | 54 | 132KV Biharsarif (SG)-Baripahari | Double | 5 | 10 | Panther | 50 | 250 | 2 | 500 | 1440 | 0 | 500
B2 | 55 | 132KV Biharsarif (SG)-Barh Ckt-I | Single | 25 | 25 | Panther | 50 | 1250 | 1 | 1250 | 720 | 0 | 1250
B3 | 56 | 132KV Barh-Hathidah Ckt-I | Single | 20 | 20 | Panther | 50 | 1000 | 1 | 1000 | 720 | 0 | 1000
B4 | 57 | 132KV Biharsarif (SG)-Hathidah Ckt-II | Single | 32.5 | 32.5 | Panther | 50 | 1625 | 1 | 1625 | 720 | 0 | 1625
B5 | 58 | 132KV Biharsarif (SG)-Ekangarsarai | Single | 30 | 30 | Panther | 50 | 1500 | 1 | 1500 | 720 | 0 | 1500
BG1 | 59 | 132KV Ekangarsarai-Hulasganj | Single | 14.5 | 14.5 | Panther | 50 | 725 | 1 | 725 | 720 | 0 | 725
B6 | 60 | 132KV Baripahari-Harnaut | Single | 26 | 26 | Panther | 50 | 1300 | 1 | 1300 | 720 | 0 | 1300
BP1 | 61 | 132KV Harnaut-Fatuha | Single | 45 | 45 | Panther | 50 | 2250 | 1 | 2250 | 720 | 0.11667 | 2249.6354
B7 | 62 | 132KV Biharsarif (SG)-Barhi (DVC)(L-28) | Single | 142 | 142 | Panther | 50 | 7100 | 1 | 7100 | 720 | 0 | 7100
B8 | 63 | 132KV Nalanda-(L-28)LILO | Double | 2 | 4 | Panther | 50 | 100 | 2 | 200 | 1440 | 0 | 200
B9 | 64 | 132KV(L -28) Line-Rajigir grid (t-connection) | Single | 6 | 6 | Panther | 50 | 300 | 1 | 300 | 720 | 0 | 300
B10 | 65 | 132KVBarhi (DVC)-Rajgir (L-29) | Single | 126 | 126 | Panther | 50 | 6300 | 1 | 6300 | 720 | 0 | 6300
B11 | 66 | 132KVRajgir-Biharsarif (L-29) | Single | 16 | 16 | Panther | 50 | 800 | 1 | 800 | 720 | 0 | 800
BG2 | 67 | 132KV Biharsarif (SG)-Nawada | Single | 41 | 41 | Panther | 50 | 2050 | 1 | 2050 | 720 | 0 | 2050
B12 | 68 | 132KV Hathidah-Lakhisarai | Single | 28 | 28 | Panther | 50 | 1400 | 1 | 1400 | 720 | 0 | 1400
B13 | 69 | 132KV Hathidah-Sheikhpura | Single | 28 | 28 | Panther | 50 | 1400 | 1 | 1400 | 720 | 0 | 1400
B14 | 70 | 132KV Lakhisarai-Jamui | Single | 35 | 35 | Panther | 50 | 1750 | 1 | 1750 | 720 | 0 | 1750 |  | 300
B15 | 71 | 132KV Biharsarif (SG)-Shekhpura | Single | 39.49 | 39.49 | Panther | 50 | 1974.5 | 1 | 1974.5 | 720 | 0 | 1974.5
B16 | 72 | 132KV Shekhpura-Jamui | Double | 52 | 104 | Panther | 50 | 2600 | 2 | 5200 | 1440 | 45.3667 | 5036.1759
D27 | 73 | 132KV Ara-Ara TSS | Single | 4.01 | 4.01 | Panther | 50 | 200.5 | 1 | 200.5 | 720 | 0 | 200.5
D28 | 74 | 132KV Dumroan-Dumroan TSS | Single | 2 | 2 | Panther | 50 | 100 | 1 | 100 | 720 | 0 | 100
G13 | 75 | 132KV Bodhgaya-Paharpur TSS | Double | 35 | 70 | Panther | 50 | 1750 | 2 | 3500 | 1440 | 0 | 3500
G14 | 76 | 132KV Rafiganj-Rafiganj TSS | Single | 4.6 | 4.6 | Panther | 50 | 230 | 1 | 230 | 720 | 0 | 230
B17 | 77 | 132KV Barh/Hathidah line-Mokama TSS | Single | 6 | 6 | Panther | 50 | 300 | 1 | 300 | 720 | 0 | 300
B18 | 78 | 132KV Lakhisarai - Lakhisarai TSS | Single | 6 | 6 | Panther | 50 | 300 | 1 | 300 | 720 | 0 | 300
B19 | 79 | 132KV Jamui-Jhajha TSS | Double | 31 | 62 | Panther | 50 | 1550 | 2 | 3100 | 1440 | 0 | 3100
P11 | 80 | 132KV Khagaul-Khagaul TSS | Single | 1 | 1 | Panther | 50 | 50 | 1 | 50 | 720 | 0 | 50
P12 | 81 | 132KV Fatuha-Khusrupur TSS | Single | 7.2 | 7.2 | Panther | 50 | 360 | 1 | 360 | 720 | 0 | 360
D29 | 82 | 132 KV Kudra- Kochas | Single | 27.43 | 27.43 | Panther | 50 | 1371.5 | 1 | 1371.5 | 720 | 0 | 1371.5
D30 | 83 | 132KV Pusouli-Sasaram | Single | 13.5 | 13.5 | Panther | 50 | 675 | 1 | 675 | 720 | 0.31667 | 674.7031
D31 | 84 | 132 KV LILO PSL-(132 KV Sasaram- Kudra TSS) | Double | 15.05 | 30.1 | Panther | 50 | 752.5 | 2 | 1505 | 1440 | 0.5 | 1504.4774
B20 | 85 | 132KV Lakhisarai(PG)- Lakhisarai | Double | 15.335 | 30.67 | Panther | 50 | 766.75 | 2 | 1533.5 | 1440 | 0 | 1533.5
B21 | 86 | 132KV Lakhisarai(PG)- Jamui | Double | 25.3 | 50.6 | Panther | 50 | 1265 | 2 | 2530 | 1440 | 0 | 2530
P13 | 87 | 132KV Sipara- Jakkanpur | Double | 18 | 36 | Panther | 50 | 900 | 2 | 1800 | 1440 | 7.6833 | 1790.3958
D32 | 88 | 132 kV Pusauli (BSPTCL)- Ramgarh | Single | 24 | 24 | Panther | 50 | 1200 | 1 | 1200 | 720 | 0 | 1200
D33 | 89 | 132 kV Ramgarh-Mohania | Single | 21.5 | 21.5 | Panther | 50 | 1075 | 1 | 1075 | 720 | 0 | 1075
D34 | 90 | 132 kV Bikramganj-Piro | Single | 21 | 21 | Panther | 50 | 1050 | 1 | 1050 | 720 | 0 | 1050
D35 | 91 | 132 kV Sonenagar(New)-Sonenagar | Double | 0.1 | 0.2 | Panther | 50 | 5 | 2 | 10 | 1440 | 0 | 10
D36 | 92 | 132 kV Pusauli- Bhabhua(Mundeshwari) | Single | 34 | 34 | Panther | 50 | 1700 | 1 | 1700 | 720 | 0 | 1700
DG4 | 93 | 132 kV Ataula - Goh | Double | 34.5 | 69 | Panther | 50 | 1725 | 2 | 3450 | 1440 | 0 | 3450
G15 | 94 | 132kv Sherghati- Sawkala(solar) | Single | 17.321 | 17.321 | Panther | 50 | 866.05 | 1 | 866.05 | 720 | 0 | 866.05
G16 | 95 | 132KV Khizirsarai(BGCL)-Wazirganj | Single | 33 | 33 | Panther | 50 | 1650 | 1 | 1650 | 720 | 0 | 1650
BH1 | 96 | 132KV Lakhisarai-Jamalpur | Single | 45 | 45 | Panther | 50 | 2250 | 1 | 2250 | 720 | 0 | 2250
BH2 | 97 | 132KV Lakhisarai-Sultanganj | Double | 79.5 | 159 | Panther | 50 | 3975 | 2 | 7950 | 1440 | 0 | 7950
H1 | 98 | 132KV Sultanganj-Tarapur(LILO from Sultanganj-Jamalpur Line at loc no.324) | Single | 21 | 21 | Panther | 50 | 1050 | 1 | 1050 | 720 | 0 | 1050
H2 | 99 | 132KV Tarapur-Jamalpur(LILO from Sultanganj-Jamalpur Line at loc no.324) | Single | 46 | 46 | Panther | 50 | 2300 | 1 | 2300 | 720 | 23.1667 | 2225.9954
H3 | 100 | 132KV Sabour-Sultanganj Ckt-I | Single | 30 | 30 | Panther | 50 | 1500 | 1 | 1500 | 720 | 0 | 1500
H4 | 101 | 132KV Sabour-Sultanganj Ckt-II | Single | 31 | 31 | Panther | 50 | 1550 | 1 | 1550 | 720 | 0 | 1550
H5 | 102 | 132KV Sultanganj-Deoghar | Single | 105 | 105 | Panther | 50 | 5250 | 1 | 5250 | 720 | 0 | 5250
H6 | 103 | 132KV KhSTSPS-Sabour | Single | 25 | 25 | Panther | 50 | 1250 | 1 | 1250 | 720 | 0 | 1250
H7 | 104 | 132KV KhSTPS- Kahalgaon | Single | 6 | 6 | Panther | 50 | 300 | 1 | 300 | 720 | 12.8833 | 294.6319
H8 | 105 | 132KV Sabour-Kahalgaon | Single | 19 | 19 | Panther | 50 | 950 | 1 | 950 | 720 | 0 | 950
H9 | 106 | 132KV Kahalgaon- Lalmatia | Single | 60 | 60 | Panther | 50 | 3000 | 1 | 3000 | 720 | 0 | 3000
H10 | 107 | 132KV Kahalgaon(BSPTCL) - Sultanganj | Double | 63.5 | 127 | Panther | 50 | 3175 | 2 | 6350 | 1440 | 0 | 6350
H11 | 108 | 132KV Banka (PG)-Sabour | Double | 41.58 | 83.16 | Panther | 50 | 2079 | 2 | 4158 | 1440 | 0 | 4158 |  | 3396.211
H12 | 109 | 132KV Banka (PG)-Banka | Double | 10 | 20 | Panther | 50 | 500 | 2 | 1000 | 1440 | 17.3333 | 987.963 |  | 3446.211
HN1 | 110 | 132KV Purnea-Naugachia (L-16) | Single | 15 | 15 | Panther | 50 | 750 | 1 | 750 | 720 | 0 | 750
N2 | 111 | 132KV Naugachia-BTPS (L-16) | Single | 35 | 35 | Panther | 50 | 1750 | 1 | 1750 | 720 | 0 | 1750
H13 | 112 | 132KV Banka(PG)-Sultanganj | Double | 45.96 | 91.92 | Panther | 50 | 2298 | 2 | 4596 | 1440 | 0 | 4596
H14 | 113 | 132KV Banka(Old)-Banka(New) | Double | 32.107 | 64.214 | Panther | 50 | 1605.35 | 2 | 3210.7 | 1440 | 0 | 3210.7
D37 | 114 | 132KV Kochas-Pusauli | Single | 27 | 27 | Panther | 50 | 1350 | 1 | 1350 | 720 | 0.91667 | 1348.2812
H15 | 115 | 132 KV Banka(New)-Jamui(New) | Double | 36.6 | 73.2 | Panther | 50 | 1830 | 2 | 3660 | 1440 | 0 | 3660
B22 | 116 | 132 KV Biharsharif-Warsaliganj | Single | 26 | 26 | Panther | 50 | 1300 | 1 | 1300 | 720 | 0 | 1300
B23 | 117 | 132 KV Warsaliganj -Nawada | Single | 13.2 | 13.2 | Panther | 50 | 660 | 1 | 660 | 720 | 0 | 660
| Total Length of 132KV Transmission Line for SBPDCL - |  |  |  | 4563.005 |  |  |  | 145 | 228150.25 | 104400 | 309.95 | 225790.0399 |  | 4459.005
| Total Number of Lines for SB = 145 | [8 empty] | Avo= | 0.98966 |  |  |  | 49
|  | 132kv Hulasganj-Hemara GIS (BGCL) | Single | 15 | 15 | Panther | UNDER BGCL
G17 | 114 | 132 kV Nawada(OLD) -Nawada(NEW) GIS Ckt-I &II | Double | 17.5 | 35 | Panther
NBPDCL | [14 empty] | 272
Line ID | Sl. No | Name of Line | Circuit | Ckt Km Length | Total length (in Km) | Conductor type | SIL | Wi ckt | Ckts | Wi | Ti | TNAi | Wi(Ti-Tnai)/Ti
N1 | 1 | 132KV Purnea (PG)-Purnea | Triple | 1.33 | 3.99 | HTLS | 50 | 66.5 | 3 | 199.5 | 2160 | 0 | 199.5
HN1 | 2 | 132KV Purnea-Naugachia (L-16) | Single | 55 | 55 | Panther | 50 | 2750 | 1 | 2750 | 720 | 0 | 2750
N2 | 3 | 132KV Naugachia-BTPS (L-16) | Single | 101 | 101 | Panther | 50 | 5050 | 1 | 5050 | 720 | 13.25 | 4957.066
N3 | 4 | 132KV Purnea-Khagaria (L-23) | Single | 150 | 150 | Panther | 50 | 7500 | 1 | 7500 | 720 | 9.25 | 7403.6458
N4 | 5 | 132KV Khagaria-BTPS (L-23) | Single | 60 | 60 | Panther | 50 | 3000 | 1 | 3000 | 720 | 3.8 | 2984.1667
N5 | 6 | 132KV Purnea-Manihari | Single | 62 | 62 | Panther | 50 | 3100 | 1 | 3100 | 720 | 0 | 3100
N36 | 7 | 132KV Manihari-Katihar | Single | 38 | 38 | Panther | 50 | 1900 | 1 | 1900 | 720 | 0 | 1900
N6 | 8 | 132KV Purnea-Dhamdaha | Single | 23 | 23 | Panther | 50 | 1150 | 1 | 1150 | 720 | 0 | 1150
N7 | 9 | 132KV Dhamdaha-Banmankhi | Single | 20.5 | 20.5 | Panther | 50 | 1025 | 1 | 1025 | 720 | 0 | 1025
N8 | 10 | 132KV Banmankhi-Saharsha | Single | 58.67 | 58.67 | Panther | 50 | 2933.5 | 1 | 2933.5 | 720 | 0 | 2933.5
N9 | 11 | 132KV Purnea-Triveniganj | Single | 93 | 93 | Panther | 50 | 4650 | 1 | 4650 | 720 | 0 | 4650
N10 | 12 | 132KV Purnea (PG)-Kishanganj | Single | 70 | 70 | Panther | 50 | 3500 | 1 | 3500 | 720 | 0 | 3500
N11 | 13 | 132KV Kishanganj-Baisi | Single | 31.6 | 31.6 | Panther | 50 | 1580 | 1 | 1580 | 720 | 0 | 1580
N12 | 14 | 132KV Kishanganj-Forbisganj | Single | 88.6 | 88.6 | Panther | 50 | 4430 | 1 | 4430 | 720 | 0 | 4430
N13 | 15 | 132KV Forbisganj-Kataya Ckt-I | Single | 39.7 | 39.7 | Panther | 50 | 1985 | 1 | 1985 | 720 | 5.2 | 1970.6639
N14 | 16 | 132KV Farbisganj-Kataya Ckt-II (old) | Single | 50.9 | 50.9 | Panther | 50 | 2545 | 1 | 2545 | 720 | 0 | 2545
N15 | 17 | 132KV Madhepura-Saharsa | Single | 50 | 50 | Panther | 50 | 2500 | 1 | 2500 | 720 | 0 | 2500
N16 | 18 | 132KV Madhepura-Sonebarsa | Single | 50 | 50 | Panther | 50 | 2500 | 1 | 2500 | 720 | 0 | 2500
N17 | 19 | 132KV Madhepura-Supoul | Double | 30 | 60 | Panther | 50 | 1500 | 2 | 3000 | 1440 | 0 | 3000
N18 | 20 | 132KV Saharsa-Uda Kishanganj | Single | 50.35 | 50.35 | Panther | 50 | 2517.5 | 1 | 2517.5 | 720 | 0 | 2517.5
N19 | 21 | 132KV Supoul-Kataya | Double | 59.6 | 119.2 | Panther | 50 | 2980 | 2 | 5960 | 1440 | 0 | 5960
N20 | 22 | 132KV BTPS-Begusarai (L-9 & L-10) | Double | 10 | 20 | Panther | 50 | 500 | 2 | 1000 | 1440 | 3.3667 | 997.662
MN1 | 23 | 132KV Begusarai-Samastipur (L-9) | Single | 57 | 57 | Panther | 50 | 2850 | 1 | 2850 | 720 | 0 | 2850
MN2 | 24 | 132KV Begusarai-Dalsingsarai (L-10) | Single | 34 | 34 | Panther | 50 | 1700 | 1 | 1700 | 720 | 0 | 1700
MN3 | 25 | 132KV Begusarai-Kuseswarsthan | Single | 65.54 | 65.54 | Panther | 50 | 3277 | 1 | 3277 | 720 | 0 | 3277
M1 | 26 | 132KV Dalsingsarai-Samastipur (L-10) | Single | 23 | 23 | Panther | 50 | 1150 | 1 | 1150 | 720 | 0 | 1150
M2 | 27 | 132KV MTPS-Samastipur | Double | 85.2 | 170.4 | Panther | 50 | 4260 | 2 | 8520 | 1440 | 22.7333 | 8385.4944
M3 | 28 | 132KV MTPS-Muzaffarpur Ckt-I | Single | 15.5 | 15.5 | Panther | 50 | 775 | 1 | 775 | 720 | 0 | 775
M4 | 29 | 132KV MTPS-Muzaffarpur Ckt-II | Single | 16.7 | 16.7 | Panther | 50 | 835 | 1 | 835 | 720 | 2.3 | 832.3326
M5 | 30 | 132KV Muzaffarpur-SKMCH | Single | 16.7 | 16.7 | Panther | 50 | 835 | 1 | 835 | 720 | 0 | 835
M6 | 31 | 132KV MTPS-SKMCH Ckt-I | Single | 14.116 | 14.116 | Panther | 50 | 705.8 | 1 | 705.8 | 720 | 4.8333 | 701.062
M7 | 32 | 132KV Samastipur -Darbhanga | Single | 40 | 40 | Panther | 50 | 2000 | 1 | 2000 | 720 | 43.5 | 1879.1667
M8 | 33 | 132KVSamastipur- Hazipur | Single | 70 | 70 | Panther | 50 | 3500 | 1 | 3500 | 720 | 46.3333 | 3274.7685
M9 | 34 | 132KV Hajipur - Jandaha | Single | 48 | 48 | Panther | 50 | 2400 | 1 | 2400 | 720 | 0 | 2400
M10 | 35 | 132 kV Jandaha-Mahnar('T'at Jandaha GSS, 12.6 KM ) | Single | 12.6 | 12.6 | Panther | 50 | 630 | 1 | 630 | 720 | 6.3333 | 624.4583
M11 | 36 | 132KV Jandaha - Samastipur | Single | 44 | 44 | Panther | 50 | 2200 | 1 | 2200 | 720 | 56.6667 | 2026.8519
M12 | 37 | 132KV Hazipur (220KV) - Hazipur (132KV) | Double | 2 | 4 | Panther | 50 | 100 | 2 | 200 | 1440 | 0 | 200
M13 | 38 | 132KV Hazipur- Chapra | Single | 57 | 57 | Panther | 50 | 2850 | 1 | 2850 | 720 | 11.9167 | 2802.8299
M14 | 39 | 132KV Chapra- Sheetalpur | Single | 28 | 28 | Panther | 50 | 1400 | 1 | 1400 | 720 | 0 | 1400
M15 | 40 | 132KV Muzaffarpur- Vaishali | Double | 30.1 | 60.2 | Panther | 50 | 1505 | 2 | 3010 | 1440 | 4.6667 | 3000.2454
M16 | 41 | 132KV Vaishali-Sheetalpur | Single | 30.21 | 30.21 | Panther | 50 | 1510.5 | 1 | 1510.5 | 720 | 0 | 1510.5
M17 | 42 | 132KV Chapra - Siwan | Single | 70 | 70 | Panther | 50 | 3500 | 1 | 3500 | 720 | 6.0333 | 3470.6713
M18 | 43 | 132KV Chapra/Siwan - Ekma | Single | 0.6 | 0.6 | Panther | 50 | 30 | 1 | 30 | 720 | 0 | 30
M19 | 44 | 132KV Mushrakh - Siwan | Single | 40 | 40 | Panther | 50 | 2000 | 1 | 2000 | 720 | 0 | 2000
M20 | 45 | 132KV Gopalganj - Mushrakh | Single | 74.866 | 74.866 | Panther | 50 | 3743.3 | 1 | 3743.3 | 720 | 0 | 3743.3
M21 | 46 | 132KV Gopalganj - Bettia ckt-I | Single | 60.75 | 60.75 | Panther | 50 | 3037.5 | 1 | 3037.5 | 720 | 0 | 3037.5
M64 | 47 | 132 kV Gopalganj- Areraj(132/33KV) CKT-II | Single | 46 | 46 | Panther | 50 | 2300 | 1 | 2300 | 720 | 0 | 2300
M65 | 48 | 132 kV Areraj(132/33KV)- Bettiah CKT-II | Single | 27 | 27 | Panther | 50 | 1350 | 1 | 1350 | 720 | 0 | 1350
M22 | 49 | 132KV Gopalganj/ Bettia Line- SUGAR MILL Sidhwalia | Single | 12 | 12 | Panther | 50 | 600 | 1 | 600 | 720 | 0 | 600
M23 | 50 | 132KV MTPS - Motipur | Single | 25.8 | 25.8 | Panther | 50 | 1290 | 1 | 1290 | 720 | 0 | 1290
M24 | 51 | 132KV Motipur-Motihari | Single | 50 | 50 | Panther | 50 | 2500 | 1 | 2500 | 720 | 1.6667 | 2494.213
M25 | 52 | 132KV Bettia - Motihari | Single | 45 | 45 | Panther | 50 | 2250 | 1 | 2250 | 720 | 0 | 2250
M26 | 53 | 132KV Bettia - Narkatiyaganj | Single | 35.85 | 35.85 | Panther | 50 | 1792.5 | 1 | 1792.5 | 720 | 0 | 1792.5
M27 | 54 | 132KV Narkatiyaganj - Ramnagar | Single | 78.59 | 78.59 | Panther | 50 | 3929.5 | 1 | 3929.5 | 720 | 9.3333 | 3878.562
M28 | 55 | 132KV Bettia - Raxaul | Double | 37.1 | 74.2 | Panther | 50 | 1855 | 2 | 3710 | 1440 | 4.75 | 3697.7622
M29 | 56 | 132KV Ramnagar - BHPC, Balmikinagar | Single | 77.77 | 77.77 | Panther | 50 | 3888.5 | 1 | 3888.5 | 720 | 0 | 3888.5
M30 | 57 | 132KV Motihari - Dhaka | Double | 24 | 48 | Panther | 50 | 1200 | 2 | 2400 | 1440 | 0 | 2400
M31 | 58 | 132KV Dhaka - Sitamarhi | Single | 50 | 50 | Panther | 50 | 2500 | 1 | 2500 | 720 | 0 | 2500
M32 | 59 | 132 kV Sitamarhi-Sheohar(LILO at loc. 79, 0.7 kM) | Single | 26.2 | 26.2 | Panther | 50 | 1310 | 1 | 1310 | 720 | 0 | 1310
M33 | 60 | 132 kV Sheohar-Dhaka | Single | 24.7 | 24.7 | Panther | 50 | 1235 | 1 | 1235 | 720 | 0 | 1235
M34 | 61 | 132KV Sitamarhi - Runisaidpur | Single | 21 | 21 | Panther | 50 | 1050 | 1 | 1050 | 720 | 34.4 | 999.8333
M35 | 62 | 132 kV SKMCH-Belsand(LILO at loc. 110/111, 11.74 kM) | Single | 42 | 42 | Panther | 50 | 2100 | 1 | 2100 | 720 | 6.6667 | 2080.5556
M36 | 63 | 132 kV Belsand-Runnisaidpur | Single | 14 | 14 | Panther | 50 | 700 | 1 | 700 | 720 | 0 | 700
M37 | 64 | 132KV SKMCH- MTPS Ckt-II | Single | 15 | 15 | Panther | 50 | 750 | 1 | 750 | 720 | 2.8 | 747.0833
M38 | 65 | 132KV Darbhanga (220KV) - Darbhanga (132KV) | Single | 1 | 1 | Panther | 50 | 50 | 1 | 50 | 720 | 0 | 50
M39 | 66 | 132 KV Darbhanga - Pandaul | Single | 29 | 29 | Panther | 50 | 1450 | 1 | 1450 | 720 | 0 | 1450
M40 | 67 | 132 KV Darbhanga - Madhubani | Single | 15.7 | 15.7 | Panther | 50 | 785 | 1 | 785 | 720 | 0 | 785
M41 | 68 | 132 KV Phoolparas - Madhubani | Single | 27.6 | 27.6 | Panther | 50 | 1380 | 1 | 1380 | 720 | 0 | 1380
M42 | 69 | 132 KV Phoolparas - Pandaul | Single | 65 | 65 | Panther | 50 | 3250 | 1 | 3250 | 720 | 0 | 3250
M43 | 70 | 132KV Gangwara - Pandaul | Single | 25.5 | 25.5 | Panther | 50 | 1275 | 1 | 1275 | 720 | 0 | 1275
M44 | 71 | 132KV Pandaul - Madhubani | Single | 16 | 16 | Panther | 50 | 800 | 1 | 800 | 720 | 0 | 800
M45 | 72 | 132KV Madhubani - Jainagar | Single | 40 | 40 | Panther | 50 | 2000 | 1 | 2000 | 720 | 0 | 2000
M46 | 73 | 132 kV Madhubani-Benipatti' T 'near GSS Madhubani | Single | 23 | 23 | Panther | 50 | 1150 | 1 | 1150 | 720 | 0 | 1150
M47 | 74 | 132KV Jainagar - Phoolparas | Single | 55 | 55 | Panther | 50 | 2750 | 1 | 2750 | 720 | 4.6667 | 2732.1759
M48 | 75 | 132KV Phoolparas - Supoul | Single | 31.92 | 31.92 | Panther | 50 | 1596 | 1 | 1596 | 720 | 0 | 1596
M49 | 76 | 132KV Chapra - Chapra TSS | Single | 1 | 1 | Panther | 50 | 50 | 1 | 50 | 720 | 0 | 50
M50 | 77 | 132KV Hazipur - Hazipur TSS | Single | 2 | 2 | Panther | 50 | 100 | 1 | 100 | 720 | 0 | 100
M51 | 78 | 132KV Darbhangha-Gangwara | Single | 19.5 | 19.5 | Panther | 50 | 975 | 1 | 975 | 720 | 7.1667 | 965.2951
N21 | 79 | 132KV Araria-Forbisganj | Single | 30 | 30 | Panther | 50 | 1500 | 1 | 1500 | 720 | 2.5833 | 1494.6181
N22 | 80 | 132KV Forbisganj-Kataya Ckt-III | Single | 39.8 | 39.8 | Panther | 50 | 1990 | 1 | 1990 | 720 | 0 | 1990
M52 | 81 | 132 kV Dalsinghsarai-Kusheshwarsthan | Single | 59.47 | 59.47 | Panther | 50 | 2973.5 | 1 | 2973.5 | 720 | 0 | 2973.5
N23 | 82 | 132KV Kataiya- Dohabi | Single | 3 | 3 | Panther | 50 | 150 | 1 | 150 | 720 | 0 | 150
N24 | 83 | 132KV Kishanganj(New)-Forbisganj | Double | 85.39 | 170.78 | Panther | 50 | 4269.5 | 2 | 8539 | 1440 | 0 | 8539
N25 | 84 | 132KV Sonebarsa-Uda Kishanganj | Double | 35.43 | 70.86 | Panther | 50 | 1771.5 | 2 | 3543 | 1440 | 0 | 3543
M53 | 85 | 132 kV (MTPS-Samastipur)-T-connection to Turki TSS | Single | 5 | 5 | Panther | 50 | 250 | 1 | 250 | 720 | 0 | 250
M54 | 86 | 132 kV Dalsingsarai- Bachhwara(TSS) | Single | 11.5 | 11.5 | Panther | 50 | 575 | 1 | 575 | 720 | 0 | 575
M55 | 87 | 132 kV Siwan-Hathua | Single | 43.91 | 43.91 | Panther | 50 | 2195.5 | 1 | 2195.5 | 720 | 0 | 2195.5
N26 | 88 | 132KV Kishanganj(New)-Kishanganj | Double | 6.9 | 13.8 | Zebra | 132 | 910.8 | 2 | 1821.6 | 1440 | 0 | 1821.6
M56 | 89 | 132KV Mushahri-SKMCH D/C | Double | 21.12 | 42.24 | Panther | 50 | 1056 | 2 | 2112 | 1440 | 1.1833 | 2110.2644
M57 | 90 | 132 KV Dhaka- Pakhridayal | Single | 18.8 | 18.8 | Panther | 50 | 940 | 1 | 940 | 720 | 0 | 940
N27 | 91 | 132KV Sonebarsa-Simri Bakhtiyarpur | Single | 14.54 | 14.54 | Panther | 50 | 727 | 1 | 727 | 720 | 0 | 727
M58 | 92 | 132KV Benipatti-Sursand (Pupri) | Single | 34.66 | 34.66 | Panther | 50 | 1733 | 1 | 1733 | 720 | 0 | 1733
N28 | 93 | 132KV Supoul - Nirmali | Single | 40 | 40 | Panther | 50 | 2000 | 1 | 2000 | 720 | 0 | 2000
N29 | 94 | 132KV Phoolparas - Nirmali | Single | 32 | 32 | Panther | 50 | 1600 | 1 | 1600 | 720 | 0 | 1600
M59 | 95 | 132 KV Vaishali- Bela rail factory | Single | 30 | 30 | Panther | 50 | 1500 | 1 | 1500 | 720 | 0 | 1500
M60 | 96 | 132 KV Sheetalpur- Bela rail factory | Single | 12 | 12 | Panther | 50 | 600 | 1 | 600 | 720 | 0 | 600
N30 | 97 | 132KV Forbisganj-Triveniganj | Single | 38 | 38 | Panther | 50 | 1900 | 1 | 1900 | 720 | 0 | 1900
M61 | 98 | 132KV Mushahri-Sitamarhi ckt-II | Double | 61 | 122 | Panther | 50 | 3050 | 2 | 6100 | 1440 | 0 | 6100
M62 | 99 | 132KV Samastipur(new)- Samastipur | Double | 7 | 14 | Zebra | 132 | 924 | 2 | 1848 | 1440 | 0 | 1848
M63 | 100 | 132KV Mashrakh- Maharajganj | Single | 18 | 18 | Panther | 50 | 900 | 1 | 900 | 720 | 0 | 900
N31 | 101 | 132 KV Begusarai- Balia | Single | 38.5 | 38.5 | Panther | 50 | 1925 | 1 | 1925 | 720 | 0 | 1925
N32 | 102 | 132 KV Begusarai-Manjhaul | Single | 16.3 | 16.3 | Panther | 50 | 815 | 1 | 815 | 720 | 0 | 815
M66 | 103 | 132 KV Motipur- Chakia | Single | 17.5 | 17.5 | Panther | 50 | 875 | 1 | 875 | 720 | 0 | 875
M67 | 104 | 132KV Gopalganj - Hathua | Single | 24.91 | 24.91 | Panther | 50 | 1245.5 | 1 | 1245.5 | 720 | 0 | 1245.5
M68 | 105 | 132KV Bettiah- Areraj (400/132KV) ckt-I | Single | 39.7 | 39.7 | Panther | 50 | 1985 | 1 | 1985 | 720 | 0 | 1985
M69 | 106 | 132KVBettiah- Areraj (400/132KV) ckt-II | Single | 39.7 | 39.7 | Panther | 50 | 1985 | 1 | 1985 | 720 | 0 | 1985
M70 | 107 | 132KV Motihari- Areraj (400/132KV) ckt-I | Single | 39 | 39 | Panther | 50 | 1950 | 1 | 1950 | 720 | 0 | 1950
M71 | 108 | 132 KV Motihari- Areraj (400/132KV) ckt-II | Single | 39 | 39 | Panther | 50 | 1950 | 1 | 1950 | 720 | 0 | 1950
M72 | 109 | 132 KV Raxaul- Parwanipur(Nepal) | Single | 6.5 | 6.5 | Panther | 50 | 325 | 1 | 325 | 720 | 0 | 325
N33 | 110 | 132 KV Kishanganj(New)- Barsoi | Single | 71.702 | 71.702 | Panther | 50 | 3585.1 | 1 | 3585.1 | 720 | 0 | 3585.1
N34 | 111 | 132 KV Begusarai- Teghra | Single | 36 | 36 | Panther | 50 | 1800 | 1 | 1800 | 720 | 0 | 1800
N35 | 112 | 132KV Kishanganj-Araria | Single | 58.5 | 58.5 | Panther | 50 | 2925 | 1 | 2925 | 720 | 14.4667 | 2866.2292
M74 | 113 | 132 kV Rosera-Kusheshwarsthan | Single | 26.4 | 26.4 | Panther | 50 | 1320 | 1 | 1320 | 720 | 9.0333 | 1303.4389
M75 | 114 | 132 kV Dalsinghsarai-Rosera | Single | 41.8 | 41.8 | Panther | 50 | 2090 | 1 | 2090 | 720 | 0 | 2090
M76 | 115 | 132 KV DMTCL- Raxaul | Double | 58.6 | 117.2 | Panther | 50 | 2930 | 2 | 5860 | 1440 | 41.4333 | 5691.3894
N37 | 116 | 132KV Saharsa-Udakishanganj ckt-II | Single | 52 | 52 | Panther | 50 | 2600 | 1 | 2600 | 720 | 0 | 2600
N38 | 117 | 132 kV Manjhaul-Bakhri | Single | 19.17 | 19.17 | Panther | 50 | 958.5 | 1 | 958.5 | 720 | 0 | 958.5
N39 | 118 | 132 kV Balia-Bakhri | Single | 25.35 | 25.35 | Panther | 50 | 1267.5 | 1 | 1267.5 | 720 | 0 | 1267.5
M78 | 119 | 132 kV Sonebarsa-Kuseshwarshtan | Double | 70 | 140 | Panther | 50 | 3500 | 2 | 7000 | 1440 | 0 | 7000
M79 | 120 | 132 kV Jainagar-Jhanjharpur (LILO at Loc No.162 at Jainagar) | Single | 80.5 | 80.5 | Panther | 50 | 4025 | 1 | 4025 | 720 | 0 | 4025
M80 | 121 | 132 kV Jhanjharpur-Phoolparas | Single | 33.5 | 33.5 | Panther | 50 | 1675 | 1 | 1675 | 720 | 0 | 1675 |  | 255.65
M81 | 122 | 132KV Samastipur(New)-Shahpurpatori | Single | 29 | 29 | Panther | 50 | 1450 | 1 | 1450 | 720 | 0 | 1450 |  | 250.73
N40 | 123 | 132KV Baisi - Dalkola (WB) | Single | 1.2 | 1.2 | Panther | 50 | 60 | 1 | 60 | 720 | 0 | 60 |  | 4.92
| Total Length of 132KV Transmission Line for NBPDCL - |  |  |  | 5271.814 |  |  |  | 141 | 265870.3 | 101520 | 380.3333 | 264475.5057
| Total Number of Lines for NB = 141 | [8 empty] | Avo= | 0.99475
M73 | 119 | 132 KV Chapra(New)-Siwan | Double | 65 | 130 | Panther | Under BGCL
M77 | 120 | 132 KV Chapra(New)-Chapra | Double | 25 | 50 | Zebra
| Total Length of 132KV Transmission Line for BSPTCL - |  |  |  | 9834.819 |  |  |  | 286 | 494020.55 |  |  | 490265.5456
| Total Number of 132 KV Lines for BSPTCL = 286 | [7 empty] | Avo= |  | 0.9924
466.1
85.7667
[10 empty] | 140 |  | 10064.819
[8 empty] | 10064.819 |  | 141
281
7

## tfmr 132
132/33 KV TFMR TAFM calculation for the month of SEP'2018
|  |  |  | 30 | days
Sl. No | Code | Name of Line | MVA | Nos. of TFMRs | Wi | Ti | TNAi | Wi(Ti-Tnai)/Ti
SBPDCL
1 | 80 MVA | 132/33 KV 80 MVA TFMR PATNA ZONE | 80 | 7 | 560 | 5040 | 1.95 | 559.7833
2 | 50 MVA | 132/33 KV 50 MVA TFMR PATNA ZONE | 50 | 88 | 4400 | 63360 | 28.95 | 4397.9896
3 | 20 MVA | 132/33 KV 20 MVA TFMR PATNA ZONE | 20 | 72 | 1440 | 51840 | 991.8333 | 1412.4491
4 | 10 MVA | 132/33 KV 10 MVA TFMR PATNA ZONE | 10 | 0 | 0 | 0 | 0 | 0
SOUTH BIHAR |  |  | (No of TRF-167) |  | 6400 |  | 1022.7333 | 6370.222
|  |  |  | Avo= | 0.99535
NBPDCL |  |  |  | 30 | days
1 | 50 MVA | 132/33 KV 50 MVA TFMR MUZ ZONE | 50 | 78 | 3900 | 56160 | 9.6667 | 3899.3287
2 | 20 MVA | 132/33 KV 20 MVA TFMR MUZ ZONE | 20 | 83 | 1660 | 59760 | 1246.1667 | 1625.3843
3 | 10 MVA | 132/33 KV 10 MVA TFMR MUZ ZONE | 10 | 6 | 60 | 4320 | 0 | 60
NORTH BIHAR |  |  | (No of TRF-167) |  | 5620 |  | 1255.8333 | 5584.713
|  |  |  | Avo= | 0.99372
|  |  | (No of TRF-334) |  | 12020 |  |  | 11954.935
|  |  | 132TF Total Avq= |  | 0.99459

## tfmr 220
220/132 KV TFMR TAFM calculation for the month of SEP'2018
|  |  |  | 30 | days
Sl. No | Code | Name of Line | MVA | Nos. of TFMRs | Wi | Ti | TNAi | Wi(Ti-Tnai)/Ti
SBPDCL
1 | 100 MVA | 220/132 KV 100 MVA TFMR PATNA ZONE | 100 | 13 | 1300 | 9360 | 784.3167 | 1191.0671
2 | 150 MVA | 220/132 KV 150 MVA TFMR PATNA ZONE | 150 | 11 | 1650 | 7920 | 16.1167 | 1646.6424
3 | 160 MVA | 220/132 KV 160 MVA TFMR PATNA ZONE | 160 | 4 | 640 | 2880 | 0 | 640
SOUTH BIHAR |  |  | (No of TRF-28) |  | 3590 |  | 800.4333 | 3477.7095
|  |  |  | Avq= | 0.96872
NBPDCL |  |  |  | 30 | days
1 | 100 MVA | 220/132 KV 100 MVA TFMR MUZ ZONE | 100 | 14 | 1400 | 10080 | 732.1667 | 1298.3102
2 | 150 MVA | 220/132 KV 150 MVA TFMR MUZ ZONE | 150 | 0 | 0 | 0 | 0 | 0
3 | 160 MVA | 220/132 KV 160 MVA TFMR MUZ ZONE | 160 | 11 | 1760 | 7920 | 722.7833 | 1599.3815
NORTH BIHAR |  |  | (No of TRF-25) |  | 3160 |  | 1454.95 | 2897.6917
|  |  |  | Avq= | 0.91699
|  |  | (No of TRF-53) |  | 6750 |  |  | 6375.4012
|  |  | 220TF Total Avq= |  | 0.9445